## Instance Map
|  | Slot | Modbus Register Start
0 Device |  | 2000 Watlow Inputs |  | 3000 Watlow Outputs |  | 4000 Watlow Mapping |  | 4001 Watlow Config |  | 6000 Inputs |  | 7000 Outputs |  | 8000 Settings |  | 5F00 Settings |  | 100
1 | 0 | 1 | 1000 | 1 | 6000 | 1 | 11000 | 1 | 16000 | 1 | 21000 | 1 | 26000 | 1 | 31000 | 1 | 36000
|  | 2 | 1100 | 2 | 6100 | 2 | 11100 | 2 | 16100 | 2 | 21100 | 2 | 26100 | 2 | 31100 | 2 | 36100
|  | 3 | 1200 | 3 | 6200 | 3 | 11200 | 3 | 16200 | 3 | 21200 | 3 | 26200 | 3 | 31200 | 3 | 36200
|  | 4 | 1300 | 4 | 6300 | 4 | 11300 | 4 | 16300 | 4 | 21300 | 4 | 26300 | 4 | 31300 | 4 | 36300
|  | 5 | 1400 | 5 | 6400 | 5 | 11400 | 5 | 16400 | 5 | 21400 | 5 | 26400 | 5 | 31400 | 5 | 36400
|  | 6 | 1500 | 6 | 6500 | 6 | 11500 | 6 | 16500 | 6 | 21500 | 6 | 26500 | 6 | 31500 | 6 | 36500
|  | 7 | 1600 | 7 | 6600 | 7 | 11600 | 7 | 16600 | 7 | 21600 | 7 | 26600 | 7 | 31600 | 7 | 36600
500 Test |  | 8 | 1700 | 8 | 6700 | 8 | 11700 | 8 | 16700 | 8 | 21700 | 8 | 26700 | 8 | 31700 | 8 | 36700
1 | 500 | 9 | 1800 | 9 | 6800 | 9 | 11800 | 9 | 16800 | 9 | 21800 | 9 | 26800 | 9 | 31800 | 9 | 36800
|  | 10 | 1900 | 10 | 6900 | 10 | 11900 | 10 | 16900 | 10 | 21900 | 10 | 26900 | 10 | 31900
|  | 11 | 2000 | 11 | 7000 | 11 | 12000 | 11 | 17000 | 11 | 22000 | 11 | 27000 | 11 | 32000
|  | 12 | 2100 | 12 | 7100 | 12 | 12100 | 12 | 17100 | 12 | 22100 | 12 | 27100 | 12 | 32100
|  | 13 | 2200 | 13 | 7200 | 13 | 12200 | 13 | 17200 | 13 | 22200 | 13 | 27200 | 13 | 32200
|  | 14 | 2300 | 14 | 7300 | 14 | 12300 | 14 | 17300 | 14 | 22300 | 14 | 27300 | 14 | 32300
|  | 15 | 2400 | 15 | 7400 | 15 | 12400 | 15 | 17400 | 15 | 22400 | 15 | 27400 | 15 | 32400
|  | 16 | 2500 | 16 | 7500 | 16 | 12500 | 16 | 17500 | 16 | 22500 | 16 | 27500 | 16 | 32500
|  | 17 | 2600 | 17 | 7600 | 17 | 12600 | 17 | 17600 | 17 | 22600 | 17 | 27600 | 17 | 32600
|  | 18 | 2700 | 18 | 7700 | 18 | 12700 | 18 | 17700 | 18 | 22700 | 18 | 27700 | 18 | 32700
|  | 19 | 2800 | 19 | 7800 | 19 | 12800 | 19 | 17800 | 19 | 22800 | 19 | 27800 | 19 | 32800
|  | 20 | 2900 | 20 | 7900 | 20 | 12900 | 20 | 17900 | 20 | 22900 | 20 | 27900 | 20 | 32900
|  | 21 | 3000 | 21 | 8000 | 21 | 13000 | 21 | 18000 | 21 | 23000 | 21 | 28000 | 21 | 33000
|  | 22 | 3100 | 22 | 8100 | 22 | 13100 | 22 | 18100 | 22 | 23100 | 22 | 28100 | 22 | 33100
|  | 23 | 3200 | 23 | 8200 | 23 | 13200 | 23 | 18200 | 23 | 23200 | 23 | 28200 | 23 | 33200
|  | 24 | 3300 | 24 | 8300 | 24 | 13300 | 24 | 18300 | 24 | 23300 | 24 | 28300 | 24 | 33300
|  | 25 | 3400 | 25 | 8400 | 25 | 13400 | 25 | 18400 | 25 | 23400 | 25 | 28400 | 25 | 33400
|  | 26 | 3500 | 26 | 8500 | 26 | 13500 | 26 | 18500 | 26 | 23500 | 26 | 28500 | 26 | 33500
|  | 27 | 3600 | 27 | 8600 | 27 | 13600 | 27 | 18600 | 27 | 23600 | 27 | 28600 | 27 | 33600
|  | 28 | 3700 | 28 | 8700 | 28 | 13700 | 28 | 18700 | 28 | 23700 | 28 | 28700 | 28 | 33700
|  | 29 | 3800 | 29 | 8800 | 29 | 13800 | 29 | 18800 | 29 | 23800 | 29 | 28800 | 29 | 33800
|  | 30 | 3900 | 30 | 8900 | 30 | 13900 | 30 | 18900 | 30 | 23900 | 30 | 28900 | 30 | 33900
|  | 31 | 4000 | 31 | 9000 | 31 | 14000 | 31 | 19000 | 31 | 24000 | 31 | 29000 | 31 | 34000
|  | 32 | 4100 | 32 | 9100 | 32 | 14100 | 32 | 19100 | 32 | 24100 | 32 | 29100 | 32 | 34100
|  | 33 | 4200 | 33 | 9200 | 33 | 14200 | 33 | 19200 | 33 | 24200 | 33 | 29200 | 33 | 34200
|  | 34 | 4300 | 34 | 9300 | 34 | 14300 | 34 | 19300 | 34 | 24300 | 34 | 29300 | 34 | 34300
|  | 35 | 4400 | 35 | 9400 | 35 | 14400 | 35 | 19400 | 35 | 24400 | 35 | 29400 | 35 | 34400
|  | 36 | 4500 | 36 | 9500 | 36 | 14500 | 36 | 19500 | 36 | 24500 | 36 | 29500 | 36 | 34500
|  | 37 | 4600 | 37 | 9600 | 37 | 14600 | 37 | 19600 | 37 | 24600 | 37 | 29600 | 37 | 34600
|  | 38 | 4700 | 38 | 9700 | 38 | 14700 | 38 | 19700 | 38 | 24700 | 38 | 29700 | 38 | 34700
|  | 39 | 4800 | 39 | 9800 | 39 | 14800 | 39 | 19800 | 39 | 24800 | 39 | 29800 | 39 | 34800
|  | 40 | 4900 | 40 | 9900 | 40 | 14900 | 40 | 19900 | 40 | 24900 | 40 | 29900 | 40 | 34900
|  | 41 | 5000 | 41 | 10000 | 41 | 15000 | 41 | 20000 | 41 | 25000 | 41 | 30000 | 41 | 35000
|  | 42 | 5100 | 42 | 10100 | 42 | 15100 | 42 | 20100 | 42 | 25100 | 42 | 30100 | 42 | 35100
|  | 43 | 5200 | 43 | 10200 | 43 | 15200 | 43 | 20200 | 43 | 25200 | 43 | 30200 | 43 | 35200
|  | 44 | 5300 | 44 | 10300 | 44 | 15300 | 44 | 20300 | 44 | 25300 | 44 | 30300 | 44 | 35300
|  | 45 | 5400 | 45 | 10400 | 45 | 15400 | 45 | 20400 | 45 | 25400 | 45 | 30400 | 45 | 35400
|  | 46 | 5500 | 46 | 10500 | 46 | 15500 | 46 | 20500 | 46 | 25500 | 46 | 30500 | 46 | 35500
|  | 47 | 5600 | 47 | 10600 | 47 | 15600 | 47 | 20600 | 47 | 25600 | 47 | 30600 | 47 | 35600
|  | 48 | 5700 | 48 | 10700 | 48 | 15700 | 48 | 20700 | 48 | 25700 | 48 | 30700 | 48 | 35700

## Device Info 0
Device Info
1 | HARDWARE_ID
2 | SOFTWARE_ID
3 | MAJOR_VERSION
4 | MINOR_VERSION
5 | BUILD_NUMBER
6 | BRANCH_NUMBER
7 | SERIAL_NUMBER_MSB
8 | SERIAL_NUMBER_LSB
9 | MFG_DATE
10 | NON_VOLATILE_SAVE
11 | RESEND_CONFIG

## Test 500
500 Test
501 | Bluetooth Available

## 0x2000 1xxx
0x2000 Watlow Inputs |  | Slot offset = 100
1001 | LIMIT_SENSOR_STATUS
1002 | OPTIC_SENSOR_STATUS
1003 | SET_POINT_RAMPING
1004 | LOOP_ERROR
1005 | LED_CURRENT
1006 | LED_CURRENT
1007 | HEATER_FAULT_CONDITION
1008 | WATCH_VARIABLE_VALUE
1009 | WATCH_VARIABLE_VALUE
1010 | LIMIT_SENSOR_VALUE
1011 | LIMIT_SENSOR_VALUE
1012 | INTERNAL_PCB_TEMPERATURE
1013 | INTERNAL_PCB_TEMPERATURE
1014 | DIRECT_ANALOG_INPUT
1015 | DIRECT_ANALOG_INPUT
Slot2
1101 | LIMIT_SENSOR_STATUS
1102 | OPTIC_SENSOR_STATUS
…
Slot3
1201 | LIMIT_SENSOR_STATUS
1202 | OPTIC_SENSOR_STATUS
…

## 0x3000 6xxx
0x3000 Watlow Outputs |  | Slot offset = 100
6001 | LOOP_ERROR_CLEAR,
6002 | CLEAR_LIMITS
6003 | SET_VARIABLE_VALUE
6004 | SET_VARIABLE_VALUE
6005 | REMOTE_LOOP_PV
6006 | REMOTE_LOOP_PV
6007 | DIRECT_ANALOG_OUTPUT
6008 | DIRECT_ANALOG_OUTPUT

## 0x4000 11xxx
0x4000 Watlow Mapping |  | Slot offset = 100
11001 | LOOP_LOCATION
11002 | SENSOR_BUS
11003 | SENSOR_ZONE
11004 | SENSOR_INSTANCE
11005 | DIGITAL_OUTPUT_BUS
11006 | DIGITAL_OUTPUT_ZONE
11007 | DIGITAL_OUTPUT_INSTANCE
11008 | ANALOG_OUTPUT_BUS
11009 | ANALOG_OUTPUT_ZONE
11010 | ANALOG_OUTPUT_INSTANCE
11011 | LIMIT_BUS
11012 | LIMIT_ZONE
11013 | LIMIT_INSTANCE
11014 | CURRENT_TRANSFORMER_BUS
11015 | CURRENT_TRANSFORMER_ZONE
11016 | CURRENT_TRANSFORMER_INSTANCE
11017 | WATCH_VARIABLE_ZONE
11018 | WATCH_VARIABLE_INSTANCE
11019 | SET_VARIABLE_ZONE
11020 | SET_VARIABLE_INSTANCE
11021 | ANALOG_PV_RETRANSMIT_BUS
11022 | ANALOG_PV_RETRANSMIT_ZONE
11023 | ANALOG_PV_RETRANSMIT_INSTANCE
11024 | COOL_DIGITAL_OUTPUT_BUS
11025 | COOL_DIGITAL_OUTPUT_ZONE
11026 | COOL_DIGITAL_OUTPUT_INSTANCE
11027 | ALARM_1_OUTPUT_BUS
11028 | ALARM_1_OUTPUT_ZONE
11029 | ALARM_1_OUTPUT_INSTANCE
11030 | ALARM_2_OUTPUT_BUS
11031 | ALARM_2_OUTPUT_ZONE
11032 | ALARM_2_OUTPUT_INSTANCE
11033 | LIMIT_OUTPUT_NUMBER
11034 | ANALOG_COOLING_OUTPUT_BUS
11035 | ANALOG_COOLING_OUTPUT_ZONE
11036 | ANALOG_COOLING_OUTPUT_INSTANCE
11037 | DIRECT_DIGITAL_INPUT_BUS
11038 | DIRECT_DIGITAL_INPUT_ZONE
11039 | DIRECT_DIGITAL_INPUT_INSTANCE
11040 | DIRECT_DIGITAL_OUTPUT_BUS
11041 | DIRECT_DIGITAL_OUTPUT_ZONE
11042 | DIRECT_DIGITAL_OUTPUT_INSTANCE
11043 | DIRECT_ANALOG_INPUT_BUS
11044 | DIRECT_ANALOG_INPUT_ZONE
11045 | DIRECT_ANALOG_INPUT_INSTANCE
11046 | DIRECT_ANALOG_OUTPUT_BUS
11047 | DIRECT_ANALOG_OUTPUT_ZONE
11048 | DIRECT_ANALOG_OUTPUT_INSTANCE

## 0x4001 16xxx
0x4001 Watlow Settings |  | Slot offset = 100
16001 | RTD_COMPENSATION
16002 | COOL_ALGORITHM
16003 | COOL_HYSTERESIS
16004 | COOL_HYSTERESIS
16005 | OPTIC_PROBE_TYPE
16006 | LIMIT_FUNCTION
16007 | LIMIT_HYSTERESIS
16008 | LIMIT_HYSTERESIS
16009 | LIMIT_HIGH_SET_POINT
16010 | LIMIT_HIGH_SET_POINT
16011 | LIMIT_LOW_SET_POINT
16012 | LIMIT_LOW_SET_POINT
16013 | HEATER_FAILURE_FUNCTION
16014 | HEATER_CURRENT_HIGH
16015 | HEATER_CURRENT_HIGH
16016 | HEATER_CURRENT_LOW
16017 | HEATER_CURRENT_LOW
16018 | CT_SCALING_HIGH
16019 | CT_SCALING_HIGH
16020 | CT_USER_OFFSET
16021 | CT_USER_OFFSET
16022 | LIMIT_SENSOR_TYPE
16023 | LIMIT_TC_TYPE
16024 | RAMP_TO_SP_ENABLE
16025 | RAMP_TO_SP_RATE
16026 | RAMP_TO_SP_RATE
16027 | HEAT_ANALOG_OUT_TYPE
16028 | HEAT_ANALOG_OUT_ELEC_HIGH
16029 | HEAT_ANALOG_OUT_ELEC_HIGH
16030 | HEAT_ANALOG_OUT_ELEC_LOW
16031 | HEAT_ANALOG_OUT_ELEC_LOW
16032 | COOL_ANALOG_OUT_TYPE
16033 | COOL_ANALOG_OUT_ELEC_HIGH
16034 | COOL_ANALOG_OUT_ELEC_HIGH
16035 | COOL_ANALOG_OUT_ELEC_LOW
16036 | COOL_ANALOG_OUT_ELEC_LOW
16037 | RETRANSMIT_OUT_TYPE
16038 | RETRANSMIT_OUT_RANGE_HIGH
16039 | RETRANSMIT_OUT_RANGE_HIGH
16040 | RETRANSMIT_OUT_RANGE_LOW
16041 | RETRANSMIT_OUT_RANGE_LOW
16042 | RETRANSMIT_OUT_ELEC_HIGH
16043 | RETRANSMIT_OUT_ELEC_HIGH
16044 | RETRANSMIT_OUT_ELEC_LOW
16045 | RETRANSMIT_OUT_ELEC_LOW
16046 | HEAT_COOL_DEADBAND
16047 | HEAT_COOL_DEADBAND
16048 | OPTICAL_LED_WARNING_POINT
16049 | OPTICAL_LED_WARNING_POINT
16050 | OPEN_LOOP_DETECT_ENABLE
16051 | OPEN_LOOP_DETECT_TIME
16052 | OPEN_LOOP_DETECT_TIME
16053 | OPEN_LOOP_DETECT_DEVIATION
16054 | OPEN_LOOP_DETECT_DEVIATION
16055 | GENERAL_INPUT_SENSOR_TYPE
16056 | GENERAL_INPUT_TC_TYPE
16057 | GENERAL_INPUT_PROCESS_HIGH
16058 | GENERAL_INPUT_PROCESS_HIGH
16059 | GENERAL_INPUT_PROCESS_LOW
16060 | GENERAL_INPUT_PROCESS_LOW

## 0x6000 21xxx
0x6000 Inputs |  | Slot offset = 100
21001 | ACTUAL_CONTROL_STATE
21002 | ACTUAL_CONTROL_LOOP_MODE
21003 | SENSOR_ERROR
21004 | TUNE_OCCURING
21005 | PROCESS_VALUE
21006 | PROCESS_VALUE
21007 | ACTUAL_POWER
21008 | ACTUAL_POWER
21009 | HEAT_POWER
21010 | HEAT_POWER
21011 | COOL_POWER
21012 | COOL_POWER
21013 | CT_READING
21014 | CT_READING
21015 | ACTIVE_CLOSED_SETPOINT
21016 | ACTIVE_CLOSED_SETPOINT
21017 | ALARM_CONDITIONS
21018 | LIMIT_CONDITIONS
21019 | DIRECT_DIGITAL_INPUT

## 0x7000 26xxx
0x7000 Outputs |  | Slot offset = 100
26001 | CONTROL_STATE
26002 | CONTROL_MODE
26003 | TARGET_SETPOINT
26004 | TARGET_SETPOINT
26005 | FORCED_MV
26006 | FORCED_MV
26007 | CLEAR_ALARMS
26008 | DIRECT DIGITAL OUTPUTS

## 0x8000 31xxx
0x8000 Setttings |  | Slot offset = 100
31001 | SENSOR_TYPE
31002 | TC_TYPE
31003 | UNITS
31004 | ALARM_1_ENABLE
31005 | ALARM_2_ENABLE
31006 | SAFE_ACTION
31007 | PROCESS_SCALE_HIGH
31008 | PROCESS_SCALE_HIGH
31009 | PROCESS_SCALE_LOW
31010 | PROCESS_SCALE_LOW
31011 | OUTPUT_1_CYCLE_TIME
31012 | OUTPUT_1_CYCLE_TIME
31013 | OUTPUT_2_CYCLE_TIME
31014 | OUTPUT_2_CYCLE_TIME
31015 | STANDBY_SET_POINT
31016 | STANDBY_SET_POINT
31017 | SP_HIGH_LIMIT
31018 | SP_HIGH_LIMIT
31019 | SP_LOW_LIMIT
31020 | SP_LOW_LIMIT
31021 | PV_BIAS
31022 | PV_BIAS
31023 | OPEN_SP_HIGH_LIMIT
31024 | OPEN_SP_HIGH_LIMIT
31025 | OPEN_SP_LOW_LIMIT
31026 | OPEN_SP_LOW_LIMIT
31027 | PROPBAND_1
31028 | PROPBAND_1
31029 | INTEGRAL_1
31030 | INTEGRAL_1
31031 | DERIVATIVE_1
31032 | DERIVATIVE_1
31033 | PROPBAND_2
31034 | PROPBAND_2
31035 | INTEGRAL_2
31036 | INTEGRAL_2
31037 | DERIVATIVE_2
31038 | DERIVATIVE_2
31039 | ALARM_1_SP_HIGH
31040 | ALARM_1_SP_HIGH
31041 | ALARM_1_SP_LOW
31042 | ALARM_1_SP_LOW
31043 | ALARM_1_SP_HIGH_LIMIT
31044 | ALARM_1_SP_HIGH_LIMIT
31045 | ALARM_1_SP_LOW_LIMIT
31046 | ALARM_1_SP_LOW_LIMIT
31047 | ALARM_2_SP_HIGH
31048 | ALARM_2_SP_HIGH
31049 | ALARM_2_SP_LOW
31050 | ALARM_2_SP_LOW
31051 | ALARM_2_SP_HIGH_LIMIT
31052 | ALARM_2_SP_HIGH_LIMIT
31053 | ALARM_2_SP_LOW_LIMIT
31054 | ALARM_2_SP_LOW_LIMIT
31055 | OVER_TEMP_SP
31056 | OVER_TEMP_SP
31057 | UNDER_TEMP_SP
31058 | UNDER_TEMP_SP

## 0x5F00 36xxx
0x5F00 Alarm Groups |  | Slot offset = 100
36001 | ALARM_GROUP_1_VALUE
36002 | ALARM_GROUP_2_VALUE
36003 | ALARM_GROUP_3_VALUE
36004 | ALARM_GROUP_4_VALUE
36005 | ALARM_GROUP_5_VALUE
36006 | ALARM_GROUP_6_VALUE
36007 | ALARM_GROUP_7_VALUE
36008 | ALARM_GROUP_8_VALUE
36009 | ALARM_GROUP_1_LOGIC
36010 | ALARM_GROUP_1_BUS
36011 | ALARM_GROUP_1_ZONE
36012 | ALARM_GROUP_1_INSTANCE
36013 | ALARM_GROUP_2_LOGIC
36014 | ALARM_GROUP_2_BUS
36015 | ALARM_GROUP_2_ZONE
36016 | ALARM_GROUP_2_INSTANCE
36017 | ALARM_GROUP_3_LOGIC
36018 | ALARM_GROUP_3_BUS
36019 | ALARM_GROUP_3_ZONE
36020 | ALARM_GROUP_3_INSTANCE
36021 | ALARM_GROUP_4_LOGIC
36022 | ALARM_GROUP_4_BUS
36023 | ALARM_GROUP_4_ZONE
36024 | ALARM_GROUP_4_INSTANCE
36025 | ALARM_GROUP_5_LOGIC
36026 | ALARM_GROUP_5_BUS
36027 | ALARM_GROUP_5_ZONE
36028 | ALARM_GROUP_5_INSTANCE
36029 | ALARM_GROUP_6_LOGIC
36030 | ALARM_GROUP_6_BUS
36031 | ALARM_GROUP_6_ZONE
36032 | ALARM_GROUP_6_INSTANCE
36033 | ALARM_GROUP_7_LOGIC
36034 | ALARM_GROUP_7_BUS
36035 | ALARM_GROUP_7_ZONE
36036 | ALARM_GROUP_7_INSTANCE
36037 | ALARM_GROUP_8_LOGIC
36038 | ALARM_GROUP_8_BUS
36039 | ALARM_GROUP_8_ZONE
36040 | ALARM_GROUP_8_INSTANCE